## PowerFlow results NODES
Name | U kV | UAngle ° | u % | Library Name | Area | Subarea | Zone
CONNECTIVITY_NODE24 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE2 | 114.2141 | -0.032403 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE84 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE18 | 114.2142 | -0.032414 | 103.8311 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE56 | 114.2138 | -0.032332 | 103.8307 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE80 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE61 | 114.2552 | -0.0071661 | 103.8684 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE40 | 114.214 | -0.032383 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE66 | 9.9999 | 0.0010463 | 99.9988 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE10 | 10.3731 | -0.56884 | 103.7313 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE65 | 9.9999 | 0.00052317 | 99.9994 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE97 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE26 | 114.2187 | -0.029603 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE101 | 114.214 | -0.032379 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE22 | 114.2551 | -0.0071276 | 103.8683 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE50 | 114.2138 | -0.032332 | 103.8307 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE23 | 114.255 | -0.0071104 | 103.8682 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE31 | 114.2553 | -0.0071819 | 103.8685 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE14 | 10.2414 | -0.71146 | 102.4143 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE43 | 114.2187 | -0.029586 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE94 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE55 | 114.2139 | -0.032356 | 103.8308 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE62 | 114.2552 | -0.0071701 | 103.8684 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE86 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE87 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE27 | 114.2188 | -0.02961 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE29 | 114.2552 | -0.0071488 | 103.8683 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE72 | 114.3112 | 0.027377 | 103.9192 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE47 | 114.2141 | -0.032386 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE44 | 114.2186 | -0.029583 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE41 | 114.2141 | -0.032386 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE77 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE32 | 114.2554 | -0.0072018 | 103.8686 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE6 | 114.3108 | 0.027443 | 103.9189 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE100 | 114.214 | -0.032379 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE25 | 114.2187 | -0.029596 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE70 | 20.9243 | 0.30683 | 99.6396 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE20 | 114.2552 | -0.0071621 | 103.8684 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE79 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE83 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE52 | 10.3788 | -0.58515 | 103.7876 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE3 | 114.2143 | -0.032426 | 103.8311 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE15 | 10.2458 | -0.72511 | 102.4582 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE17 | 114.2141 | -0.032397 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE93 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE1 | 114.214 | -0.032379 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE90 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE34 | 114.3108 | 0.02744 | 103.919 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE53 | 10.38 | -0.58793 | 103.7999 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE46 | 114.214 | -0.032383 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE89 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE28 | 114.2552 | -0.0071554 | 103.8684 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE11 | 10.3687 | -0.55529 | 103.6874 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE49 | 114.2139 | -0.032356 | 103.8308 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE69 | 20.9255 | 0.30552 | 99.6453 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE38 | 114.2186 | -0.029583 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE35 | 114.3107 | 0.02746 | 103.9189 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE21 | 114.2552 | -0.0071448 | 103.8683 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE19 | 114.2142 | -0.032431 | 103.8311 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE96 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE7 | 114.3107 | 0.027467 | 103.9188 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE59 | 10.38 | -0.58793 | 103.7999 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE76 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE73 | 114.3114 | 0.027334 | 103.9194 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE37 | 114.2187 | -0.029586 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE58 | 10.3788 | -0.58515 | 103.7876 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE60 | 10.3812 | -0.5907 | 103.8122 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE48 | 114.2141 | -0.032389 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE88 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE4 | 114.2144 | -0.032449 | 103.8313 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE91 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE16 | 10.2502 | -0.73875 | 102.5022 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE36 | 114.3106 | 0.02748 | 103.9188 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE85 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE98 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE81 | 114.2187 | -0.02959 | 103.8352 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE68 | 20.9267 | 0.30421 | 99.651 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE51 | 114.2137 | -0.032309 | 103.8306 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE67 | 9.9998 | 0.0015695 | 99.9982 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE54 | 10.3812 | -0.5907 | 103.8122 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE45 | 114.2186 | -0.02958 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE64 | 10 | 0 | 100 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE33 | 114.2555 | -0.0072216 | 103.8687 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE71 | 20.9231 | 0.30814 | 99.6339 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE95 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE8 | 114.3106 | 0.02749 | 103.9187 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE57 | 114.2137 | -0.032309 | 103.8306 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE63 | 114.2552 | -0.0071741 | 103.8684 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE42 | 114.2141 | -0.032389 | 103.831 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE30 | 114.2551 | -0.0071422 | 103.8683 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE82 | 380.7289 | -0.02959 | 100.1918 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE78 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE5 | 114.311 | 0.02742 | 103.919 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE92 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE12 | 10.3644 | -0.54173 | 103.6435 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE102 | 114.214 | -0.032379 | 103.8309 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE9 | 10.3775 | -0.58238 | 103.7752 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE39 | 114.2186 | -0.02958 | 103.8351 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE13 | 10.237 | -0.6978 | 102.3703 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE75 | 28.5547 | -0.02959 | 95.1822 | - | AA | Z1 | _CA_A1
CONNECTIVITY_NODE74 | 114.3116 | 0.02729 | 103.9196 | - | AA | Z1 | _CA_A1

## PowerFlow results ELEMENTS
Name | Element Type | Nodes | P MW | Q Mvar | I A | IAngle ° | Loading % | PLosses MW | QLosses Mvar | Library Name | Area | Subarea | Zone
BREAKER14 | Circuit breaker | CONNECTIVITY_NODE46 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.3165e-08 | 4.3368e-17 | - | AA | Z1 | _CA_A1
BREAKER14 | Circuit breaker | CONNECTIVITY_NODE47 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.3165e-08 | 4.3368e-17 | - | AA | Z1 | _CA_A1
BREAKER16 | Circuit breaker | CONNECTIVITY_NODE52 | -2.557 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER16 | Circuit breaker | CONNECTIVITY_NODE53 | 2.5574 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER18 | Circuit breaker | CONNECTIVITY_NODE58 | -2.557 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER18 | Circuit breaker | CONNECTIVITY_NODE59 | 2.5574 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER1 | Circuit breaker | CONNECTIVITY_NODE2 | -2.6887 | -1.0609 | 14.6113 | 158.4353 | 0 | 3.2023e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER1 | Circuit breaker | CONNECTIVITY_NODE3 | 2.6887 | 1.0609 | 14.6113 | -21.5647 | 0 | 3.2023e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER15 | Circuit breaker | CONNECTIVITY_NODE49 | 2.559 | 1.0732 | 14.027 | -22.7852 | 0 | 2.9517e-06 | 0 | - | AA | Z1 | _CA_A1
BREAKER15 | Circuit breaker | CONNECTIVITY_NODE50 | -2.5589 | -1.0732 | 14.027 | 157.2148 | 0 | 2.9517e-06 | 0 | - | AA | Z1 | _CA_A1
BREAKER17 | Circuit breaker | CONNECTIVITY_NODE55 | 2.559 | 1.0732 | 14.027 | -22.7852 | 0 | 2.9513e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER17 | Circuit breaker | CONNECTIVITY_NODE56 | -2.5589 | -1.0732 | 14.027 | 157.2148 | 0 | 2.9513e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER19 | Circuit breaker | CONNECTIVITY_NODE61 | -0.12303 | -0.18255 | 1.1124 | 123.9698 | 0 | 1.9423e-08 | 0 | - | AA | Z1 | _CA_A1
BREAKER19 | Circuit breaker | CONNECTIVITY_NODE62 | 0.12303 | 0.18255 | 1.1124 | -56.0302 | 0 | 1.9423e-08 | 0 | - | AA | Z1 | _CA_A1
BREAKER10 | Circuit breaker | CONNECTIVITY_NODE34 | 2.3071 | 0.90628 | 12.5193 | -21.4184 | 0 | 2.3513e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER10 | Circuit breaker | CONNECTIVITY_NODE35 | -2.3071 | -0.90628 | 12.5193 | 158.5816 | 0 | 2.3513e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER11 | Circuit breaker | CONNECTIVITY_NODE37 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.2447e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
BREAKER11 | Circuit breaker | CONNECTIVITY_NODE38 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.2447e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
BREAKER13 | Circuit breaker | CONNECTIVITY_NODE43 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.2447e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
BREAKER13 | Circuit breaker | CONNECTIVITY_NODE44 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.2447e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
BREAKER12 | Circuit breaker | CONNECTIVITY_NODE40 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.3165e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
BREAKER12 | Circuit breaker | CONNECTIVITY_NODE41 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.3165e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR56 | Disconnect Switch | CONNECTIVITY_NODE94 | 1.2487e-11 | -5.6355e-19 | 2.5248e-10 | -90 | 0 | -5.5167e-12 | 2.1924e-18 | - | AA | Z1 | _CA_A1
DISCONNECTOR56 | Disconnect Switch | CONNECTIVITY_NODE95 | -1.8004e-11 | 2.756e-18 | 3.6403e-10 | 90 | 0 | -5.5167e-12 | 2.1924e-18 | - | AA | Z1 | _CA_A1
DISCONNECTOR31 | Disconnect Switch | CONNECTIVITY_NODE9 | -2.5566 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR31 | Disconnect Switch | CONNECTIVITY_NODE52 | 2.557 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR52 | Disconnect Switch | CONNECTIVITY_NODE87 | 2.0614e-08 | -7.8132e-14 | 3.126e-08 | -90 | 0 | -8.6622e-09 | -1.0824e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR52 | Disconnect Switch | CONNECTIVITY_NODE88 | -2.9276e-08 | 7.8024e-14 | 4.4396e-08 | 90 | 0 | -8.6622e-09 | -1.0824e-16 | - | AA | Z1 | _CA_A1
BREAKER7 | Circuit breaker | CONNECTIVITY_NODE25 | -0.74895 | -0.30186 | 4.0817 | 158.0185 | 0 | 2.5025e-07 | 2.1684e-16 | - | AA | Z1 | _CA_A1
BREAKER7 | Circuit breaker | CONNECTIVITY_NODE26 | 0.74895 | 0.30186 | 4.0817 | -21.9815 | 0 | 2.5025e-07 | 2.1684e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR37 | Disconnect Switch | CONNECTIVITY_NODE20 | -0.12303 | -0.18255 | 1.1124 | 123.9698 | 0 | 1.8603e-08 | 4.3368e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR37 | Disconnect Switch | CONNECTIVITY_NODE61 | 0.12303 | 0.18255 | 1.1124 | -56.0302 | 0 | 1.8603e-08 | 4.3368e-17 | - | AA | Z1 | _CA_A1
BREAKER29 | Circuit breaker | CONNECTIVITY_NODE96 | 1.3088e-09 | -1.6353e-17 | 1.9847e-09 | -90 | 0 | 2.2957e-09 | -3.2706e-17 | - | AA | Z1 | _CA_A1
BREAKER29 | Circuit breaker | CONNECTIVITY_NODE97 | 9.8692e-10 | -1.6353e-17 | 1.4966e-09 | -90 | 0 | 2.2957e-09 | -3.2706e-17 | - | AA | Z1 | _CA_A1
BREAKER23 | Circuit breaker | CONNECTIVITY_NODE76 | -8.1094e-12 | 4.2481e-19 | 1.6397e-10 | 90 | 0 | 1.7522e-11 | 3.0805e-18 | - | AA | Z1 | _CA_A1
BREAKER23 | Circuit breaker | CONNECTIVITY_NODE77 | 2.5631e-11 | 2.6557e-18 | 5.1824e-10 | -90 | 0 | 1.7522e-11 | 3.0805e-18 | - | AA | Z1 | _CA_A1
T5 | 2W transformer | CONNECTIVITY_NODE51 | 2.5589 | 1.0732 | 14.027 | -22.7852 | 0 | 0.0012391 | 0.029713 | - | AA | Z1 | _CA_A1
T5 | 2W transformer | CONNECTIVITY_NODE54 | -2.5577 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.0012391 | 0.029713 | - | AA | Z1 | _CA_A1
DISCONNECTOR54 | Disconnect Switch | CONNECTIVITY_NODE90 | -2.9295e-08 | 7.6113e-13 | 1.4808e-07 | 90 | 0 | -6.4546e-13 | 7.7993e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR54 | Disconnect Switch | CONNECTIVITY_NODE91 | 2.9294e-08 | -7.6106e-13 | 1.4808e-07 | -90 | 0 | -6.4546e-13 | 7.7993e-17 | - | AA | Z1 | _CA_A1
BREAKER25 | Circuit breaker | CONNECTIVITY_NODE83 | 1.1167e-08 | 7.7948e-14 | 1.6934e-08 | -90 | 0 | -9.0407e-09 | 7.6779e-17 | - | AA | Z1 | _CA_A1
BREAKER25 | Circuit breaker | CONNECTIVITY_NODE84 | -2.0208e-08 | -7.7871e-14 | 3.0644e-08 | 90 | 0 | -9.0407e-09 | 7.6779e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR48 | Disconnect Switch | CONNECTIVITY_NODE80 | -2.921e-08 | 3.3142e-13 | 1.4765e-07 | 90 | 0 | 2.7266e-11 | 7.2873e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR48 | Disconnect Switch | CONNECTIVITY_NODE81 | 2.9238e-08 | -3.3134e-13 | 1.4779e-07 | -90 | 0 | 2.7266e-11 | 7.2873e-17 | - | AA | Z1 | _CA_A1
L6 | Line | CONNECTIVITY_NODE12 | 9.0981 | 5.087 | 580.6551 | -29.7524 | 0 | 0.082941 | 0.086987 | - | AA | Z1 | _CA_A1
L6 | Line | CONNECTIVITY_NODE16 | -9.0152 | -5 | 580.6551 | 150.2476 | 0 | 0.082941 | 0.086987 | - | AA | Z1 | _CA_A1
DISCONNECTOR47 | Disconnect Switch | CONNECTIVITY_NODE24 | -3.0022e-08 | 3.3144e-13 | 1.5175e-07 | 90 | 0 | -4.3396e-10 | 5.7182e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR47 | Disconnect Switch | CONNECTIVITY_NODE79 | 2.9588e-08 | -3.3139e-13 | 1.4956e-07 | -90 | 0 | -4.3396e-10 | 5.7182e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR25 | Disconnect Switch | CONNECTIVITY_NODE24 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.219e-08 | -6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR25 | Disconnect Switch | CONNECTIVITY_NODE43 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.219e-08 | -6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR29 | Disconnect Switch | CONNECTIVITY_NODE1 | 2.559 | 1.0732 | 14.027 | -22.7852 | 0 | 2.9516e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR29 | Disconnect Switch | CONNECTIVITY_NODE49 | -2.559 | -1.0732 | 14.027 | 157.2148 | 0 | 2.9516e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR50 | Disconnect Switch | CONNECTIVITY_NODE84 | 2.0208e-08 | 7.7871e-14 | 3.0644e-08 | -90 | 0 | -9.0685e-09 | 6.5947e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR50 | Disconnect Switch | CONNECTIVITY_NODE85 | -2.9276e-08 | -7.7805e-14 | 4.4396e-08 | 90 | 0 | -9.0685e-09 | 6.5947e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR5 | Disconnect Switch | CONNECTIVITY_NODE9 | 9.1133 | 5.087 | 580.6551 | -29.7524 | 0 | 0.0050574 | 1.3878e-15 | - | AA | Z1 | _CA_A1
DISCONNECTOR5 | Disconnect Switch | CONNECTIVITY_NODE10 | -9.1082 | -5.087 | 580.6551 | 150.2476 | 0 | 0.0050574 | 1.3878e-15 | - | AA | Z1 | _CA_A1
DISCONNECTOR59 | Disconnect Switch | CONNECTIVITY_NODE1 | -1.2937e-10 | 1.7876e-17 | 6.5397e-10 | 90 | 0 | -1.388e-10 | 1.0137e-18 | - | AA | Z1 | _CA_A1
DISCONNECTOR59 | Disconnect Switch | CONNECTIVITY_NODE100 | -9.4297e-12 | -1.6862e-17 | 4.7667e-11 | 90 | 0 | -1.388e-10 | 1.0137e-18 | - | AA | Z1 | _CA_A1
DISCONNECTOR13 | Disconnect Switch | CONNECTIVITY_NODE24 | -0.74895 | -0.30186 | 4.0817 | 158.0185 | 0 | 2.4977e-07 | -4.3368e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR13 | Disconnect Switch | CONNECTIVITY_NODE25 | 0.74895 | 0.30186 | 4.0817 | -21.9815 | 0 | 2.4977e-07 | -4.3368e-17 | - | AA | Z1 | _CA_A1
BREAKER22 | Circuit breaker | CONNECTIVITY_NODE72 | -4.997 | -1.9709 | 27.1306 | 158.5028 | 0 | 1.1042e-05 | -6.9389e-16 | - | AA | Z1 | _CA_A1
BREAKER22 | Circuit breaker | CONNECTIVITY_NODE73 | 4.997 | 1.9709 | 27.1306 | -21.4972 | 0 | 1.1042e-05 | -6.9389e-16 | - | AA | Z1 | _CA_A1
T2 | 2W transformer | CONNECTIVITY_NODE63 | -0.12303 | -0.18255 | 1.1124 | 123.9698 | 0 | 2.6729e-06 | 6.4093e-05 | - | AA | Z1 | _CA_A1
T2 | 2W transformer | CONNECTIVITY_NODE67 | 0.12303 | 0.18262 | 12.7132 | -56.0302 | 0 | 2.6729e-06 | 6.4093e-05 | - | AA | Z1 | _CA_A1
BREAKER30 | Circuit breaker | CONNECTIVITY_NODE100 | 9.4297e-12 | 1.6862e-17 | 4.7667e-11 | -90 | 0 | -3.2201e-12 | 1.7888e-17 | - | AA | Z1 | _CA_A1
BREAKER30 | Circuit breaker | CONNECTIVITY_NODE101 | -1.265e-11 | 1.0256e-18 | 6.3944e-11 | 90 | 0 | -3.2201e-12 | 1.7888e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR2 | Disconnect Switch | CONNECTIVITY_NODE3 | -2.6887 | -1.0609 | 14.6113 | 158.4353 | 0 | 3.2023e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR2 | Disconnect Switch | CONNECTIVITY_NODE4 | 2.6887 | 1.0609 | 14.6113 | -21.5647 | 0 | 3.2023e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
T4 | 3W transformer | CONNECTIVITY_NODE78 | -3.8793e-11 | -3.3267e-18 | 7.8436e-10 | 90 | 0 | -1.495e-14 | 4.0915e-13 | - | AA | Z1 | _CA_A1
T4 | 3W transformer | CONNECTIVITY_NODE81 | -2.9238e-08 | 3.3134e-13 | 1.4779e-07 | 90 | 0 | -1.495e-14 | 4.0915e-13 | - | AA | Z1 | _CA_A1
T4 | 3W transformer | CONNECTIVITY_NODE85 | 2.9276e-08 | 7.7805e-14 | 4.4396e-08 | -90 | 0 | -1.495e-14 | 4.0915e-13 | - | AA | Z1 | _CA_A1
DISCONNECTOR3 | Disconnect Switch | CONNECTIVITY_NODE5 | 2.6899 | 1.0646 | 14.6113 | -21.5647 | 0 | 3.2018e-06 | 3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR3 | Disconnect Switch | CONNECTIVITY_NODE6 | -2.6899 | -1.0646 | 14.6113 | 158.4353 | 0 | 3.2018e-06 | 3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER3 | Circuit breaker | CONNECTIVITY_NODE10 | 9.1082 | 5.087 | 580.6551 | -29.7524 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
BREAKER3 | Circuit breaker | CONNECTIVITY_NODE11 | -9.1032 | -5.087 | 580.6551 | 150.2476 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR22 | Disconnect Switch | CONNECTIVITY_NODE38 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.3107e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR22 | Disconnect Switch | CONNECTIVITY_NODE39 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.3107e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR55 | Disconnect Switch | CONNECTIVITY_NODE92 | 0 | 0 | 0 | 90 | 0 | -2.995e-12 | -6.7205e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR55 | Disconnect Switch | CONNECTIVITY_NODE93 | -2.995e-12 | -6.7205e-19 | 6.0555e-11 | 90 | 0 | -2.995e-12 | -6.7205e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR18 | Disconnect Switch | CONNECTIVITY_NODE32 | -2.3065 | -0.90444 | 12.5193 | 158.5816 | 0 | 2.3508e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR18 | Disconnect Switch | CONNECTIVITY_NODE33 | 2.3065 | 0.90444 | 12.5193 | -21.4184 | 0 | 2.3508e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR9 | Disconnect Switch | CONNECTIVITY_NODE1 | -1.6802 | -0.78372 | 9.3721 | 154.9616 | 0 | 1.3177e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR9 | Disconnect Switch | CONNECTIVITY_NODE17 | 1.6802 | 0.78372 | 9.3721 | -25.0384 | 0 | 1.3177e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR43 | Disconnect Switch | CONNECTIVITY_NODE5 | -4.997 | -1.9709 | 27.1306 | 158.5028 | 0 | 1.104e-05 | 6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR43 | Disconnect Switch | CONNECTIVITY_NODE72 | 4.997 | 1.9709 | 27.1306 | -21.4972 | 0 | 1.104e-05 | 6.9389e-16 | - | AA | Z1 | _CA_A1
L1 | Line | CONNECTIVITY_NODE27 | -0.74895 | -0.30186 | 4.0817 | 158.0185 | 0 | 0.00011995 | 0.00038985 | - | AA | Z1 | _CA_A1
L1 | Line | CONNECTIVITY_NODE30 | 0.74907 | 0.30225 | 4.0817 | -21.9815 | 0 | 0.00011995 | 0.00038985 | - | AA | Z1 | _CA_A1
DISCONNECTOR38 | Disconnect Switch | CONNECTIVITY_NODE62 | -0.12303 | -0.18255 | 1.1124 | 123.9698 | 0 | 1.8564e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR38 | Disconnect Switch | CONNECTIVITY_NODE63 | 0.12303 | 0.18255 | 1.1124 | -56.0302 | 0 | 1.8564e-08 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR14 | Disconnect Switch | CONNECTIVITY_NODE26 | -0.74895 | -0.30186 | 4.0817 | 158.0185 | 0 | 2.4956e-07 | -4.3368e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR14 | Disconnect Switch | CONNECTIVITY_NODE27 | 0.74895 | 0.30186 | 4.0817 | -21.9815 | 0 | 2.4956e-07 | -4.3368e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR23 | Disconnect Switch | CONNECTIVITY_NODE1 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.2666e-08 | -9.194e-15 | - | AA | Z1 | _CA_A1
DISCONNECTOR23 | Disconnect Switch | CONNECTIVITY_NODE40 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.2666e-08 | -9.194e-15 | - | AA | Z1 | _CA_A1
BREAKER27 | Circuit breaker | CONNECTIVITY_NODE89 | -2.9541e-08 | 7.6098e-13 | 1.4932e-07 | 90 | 0 | -2.4637e-10 | -1.5316e-16 | - | AA | Z1 | _CA_A1
BREAKER27 | Circuit breaker | CONNECTIVITY_NODE90 | 2.9295e-08 | -7.6113e-13 | 1.4808e-07 | -90 | 0 | -2.4637e-10 | -1.5316e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR42 | Disconnect Switch | CONNECTIVITY_NODE70 | 4.9993 | 2 | 148.5721 | -21.4972 | 0 | 0.00033111 | 3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR42 | Disconnect Switch | CONNECTIVITY_NODE71 | -4.999 | -2 | 148.5721 | 158.5028 | 0 | 0.00033111 | 3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR57 | Disconnect Switch | CONNECTIVITY_NODE82 | -7.5193e-09 | -1.7757e-28 | 1.1402e-08 | 90 | 0 | -8.8281e-09 | 1.6353e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR57 | Disconnect Switch | CONNECTIVITY_NODE96 | -1.3088e-09 | 1.6353e-17 | 1.9847e-09 | 90 | 0 | -8.8281e-09 | 1.6353e-17 | - | AA | Z1 | _CA_A1
M2a | Asynchronous machine | CONNECTIVITY_NODE13 | 2 | 1 | 126.1102 | -27.2628 | 93.9986 | 0 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR7 | Disconnect Switch | CONNECTIVITY_NODE13 | -9 | -5 | 580.6551 | 150.2476 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR7 | Disconnect Switch | CONNECTIVITY_NODE14 | 9.0051 | 5 | 580.6551 | -29.7524 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
BREAKER2 | Circuit breaker | CONNECTIVITY_NODE6 | 2.6899 | 1.0646 | 14.6113 | -21.5647 | 0 | 3.2029e-06 | 0 | - | AA | Z1 | _CA_A1
BREAKER2 | Circuit breaker | CONNECTIVITY_NODE7 | -2.6899 | -1.0646 | 14.6113 | 158.4353 | 0 | 3.2029e-06 | 0 | - | AA | Z1 | _CA_A1
T3 | 3W transformer | CONNECTIVITY_NODE88 | 2.9276e-08 | -7.8024e-14 | 4.4396e-08 | -90 | 0 | -3.8918e-15 | 6.8303e-13 | - | AA | Z1 | _CA_A1
T3 | 3W transformer | CONNECTIVITY_NODE91 | -2.9294e-08 | 7.6106e-13 | 1.4808e-07 | 90 | 0 | -3.8918e-15 | 6.8303e-13 | - | AA | Z1 | _CA_A1
T3 | 3W transformer | CONNECTIVITY_NODE95 | 1.8004e-11 | -2.756e-18 | 3.6403e-10 | -90 | 0 | -3.8918e-15 | 6.8303e-13 | - | AA | Z1 | _CA_A1
DISCONNECTOR24 | Disconnect Switch | CONNECTIVITY_NODE41 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.2403e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR24 | Disconnect Switch | CONNECTIVITY_NODE42 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.2403e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
BREAKER26 | Circuit breaker | CONNECTIVITY_NODE86 | 1.219e-08 | -7.8039e-14 | 1.8486e-08 | -90 | 0 | -8.4239e-09 | 9.2829e-17 | - | AA | Z1 | _CA_A1
BREAKER26 | Circuit breaker | CONNECTIVITY_NODE87 | -2.0614e-08 | 7.8132e-14 | 3.126e-08 | 90 | 0 | -8.4239e-09 | 9.2829e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR51 | Disconnect Switch | CONNECTIVITY_NODE82 | 4.4865e-09 | -7.7882e-14 | 6.8035e-09 | -90 | 0 | -7.7037e-09 | 1.5746e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR51 | Disconnect Switch | CONNECTIVITY_NODE86 | -1.219e-08 | 7.8039e-14 | 1.8486e-08 | 90 | 0 | -7.7037e-09 | 1.5746e-16 | - | AA | Z1 | _CA_A1
L2 | Line | CONNECTIVITY_NODE33 | -2.3065 | -0.90444 | 12.5193 | 158.5816 | 0 | 0.00056424 | 0.0018338 | - | AA | Z1 | _CA_A1
L2 | Line | CONNECTIVITY_NODE36 | 2.3071 | 0.90628 | 12.5193 | -21.4184 | 0 | 0.00056424 | 0.0018338 | - | AA | Z1 | _CA_A1
DISCONNECTOR10 | Disconnect Switch | CONNECTIVITY_NODE18 | -1.6802 | -0.78372 | 9.3721 | 154.9616 | 0 | 1.3177e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR10 | Disconnect Switch | CONNECTIVITY_NODE19 | 1.6802 | 0.78372 | 9.3721 | -25.0384 | 0 | 1.3177e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER5 | Circuit breaker | CONNECTIVITY_NODE17 | -1.6802 | -0.78372 | 9.3721 | 154.9616 | 0 | 1.3179e-06 | 3.3827e-14 | - | AA | Z1 | _CA_A1
BREAKER5 | Circuit breaker | CONNECTIVITY_NODE18 | 1.6802 | 0.78372 | 9.3721 | -25.0384 | 0 | 1.3179e-06 | 3.3827e-14 | - | AA | Z1 | _CA_A1
DISCONNECTOR15 | Disconnect Switch | CONNECTIVITY_NODE20 | 0.74907 | 0.30225 | 4.0817 | -21.9815 | 0 | 2.5013e-07 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR15 | Disconnect Switch | CONNECTIVITY_NODE28 | -0.74907 | -0.30225 | 4.0817 | 158.0185 | 0 | 2.5013e-07 | 0 | - | AA | Z1 | _CA_A1
BREAKER8 | Circuit breaker | CONNECTIVITY_NODE28 | 0.74907 | 0.30225 | 4.0817 | -21.9815 | 0 | 2.4942e-07 | 4.3368e-17 | - | AA | Z1 | _CA_A1
BREAKER8 | Circuit breaker | CONNECTIVITY_NODE29 | -0.74907 | -0.30225 | 4.0817 | 158.0185 | 0 | 2.4942e-07 | 4.3368e-17 | - | AA | Z1 | _CA_A1
L5 | Line | CONNECTIVITY_NODE4 | -2.6887 | -1.0609 | 14.6113 | 158.4353 | 0 | 0.0011528 | 0.0037083 | - | AA | Z1 | _CA_A1
L5 | Line | CONNECTIVITY_NODE8 | 2.6899 | 1.0646 | 14.6113 | -21.5647 | 0 | 0.0011528 | 0.0037083 | - | AA | Z1 | _CA_A1
G2 | Synchronous machine | CONNECTIVITY_NODE64 | -0.12304 | -0.18262 | 12.7132 | 123.9698 | 0.15414 | 0 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR36 | Disconnect Switch | CONNECTIVITY_NODE59 | -2.5574 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR36 | Disconnect Switch | CONNECTIVITY_NODE60 | 2.5577 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR60 | Disconnect Switch | CONNECTIVITY_NODE101 | 1.265e-11 | -1.0256e-18 | 6.3944e-11 | -90 | 0 | 1.265e-11 | -1.0256e-18 | - | AA | Z1 | _CA_A1
DISCONNECTOR60 | Disconnect Switch | CONNECTIVITY_NODE102 | 0 | 0 | 0 | 90 | 0 | 1.265e-11 | -1.0256e-18 | - | AA | Z1 | _CA_A1
BREAKER4 | Circuit breaker | CONNECTIVITY_NODE14 | -9.0051 | -5 | 580.6551 | 150.2476 | 0 | 0.0050574 | 0 | - | AA | Z1 | _CA_A1
BREAKER4 | Circuit breaker | CONNECTIVITY_NODE15 | 9.0101 | 5 | 580.6551 | -29.7524 | 0 | 0.0050574 | 0 | - | AA | Z1 | _CA_A1
G1 | Synchronous machine | CONNECTIVITY_NODE68 | -5 | -2 | 148.5721 | 158.5028 | 3.6027 | 0 | 0 | - | AA | Z1 | _CA_A1
T1 | 2W transformer | CONNECTIVITY_NODE71 | 4.999 | 2 | 148.5721 | -21.4972 | 0 | 0.0019469 | 0.029139 | - | AA | Z1 | _CA_A1
T1 | 2W transformer | CONNECTIVITY_NODE74 | -4.9971 | -1.9709 | 27.1306 | 158.5028 | 0 | 0.0019469 | 0.029139 | - | AA | Z1 | _CA_A1
DISCONNECTOR11 | Disconnect Switch | CONNECTIVITY_NODE20 | 1.6805 | 0.78474 | 9.3721 | -25.0384 | 0 | 1.3177e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR11 | Disconnect Switch | CONNECTIVITY_NODE21 | -1.6805 | -0.78474 | 9.3721 | 154.9616 | 0 | 1.3177e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR1 | Disconnect Switch | CONNECTIVITY_NODE1 | -2.6887 | -1.0609 | 14.6113 | 158.4353 | 0 | 3.2023e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR1 | Disconnect Switch | CONNECTIVITY_NODE2 | 2.6887 | 1.0609 | 14.6113 | -21.5647 | 0 | 3.2023e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR45 | Disconnect Switch | CONNECTIVITY_NODE75 | 0 | 0 | 0 | 90 | 0 | 8.1094e-12 | -4.2481e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR45 | Disconnect Switch | CONNECTIVITY_NODE76 | 8.1094e-12 | -4.2481e-19 | 1.6397e-10 | -90 | 0 | 8.1094e-12 | -4.2481e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR44 | Disconnect Switch | CONNECTIVITY_NODE73 | -4.997 | -1.9709 | 27.1306 | 158.5028 | 0 | 1.104e-05 | 6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR44 | Disconnect Switch | CONNECTIVITY_NODE74 | 4.9971 | 1.9709 | 27.1306 | -21.4972 | 0 | 1.104e-05 | 6.9389e-16 | - | AA | Z1 | _CA_A1
BREAKER9 | Circuit breaker | CONNECTIVITY_NODE31 | -2.3065 | -0.90444 | 12.5193 | 158.5816 | 0 | 2.3511e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER9 | Circuit breaker | CONNECTIVITY_NODE32 | 2.3065 | 0.90444 | 12.5193 | -21.4184 | 0 | 2.3511e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR33 | Disconnect Switch | CONNECTIVITY_NODE1 | 2.559 | 1.0732 | 14.027 | -22.7852 | 0 | 2.9516e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR33 | Disconnect Switch | CONNECTIVITY_NODE55 | -2.559 | -1.0732 | 14.027 | 157.2148 | 0 | 2.9516e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR16 | Disconnect Switch | CONNECTIVITY_NODE29 | 0.74907 | 0.30225 | 4.0817 | -21.9815 | 0 | 2.504e-07 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR16 | Disconnect Switch | CONNECTIVITY_NODE30 | -0.74907 | -0.30225 | 4.0817 | 158.0185 | 0 | 2.504e-07 | 0 | - | AA | Z1 | _CA_A1
BREAKER21 | Circuit breaker | CONNECTIVITY_NODE69 | 4.9997 | 2 | 148.5721 | -21.4972 | 0 | 0.00033111 | 3.4694e-16 | - | AA | Z1 | _CA_A1
BREAKER21 | Circuit breaker | CONNECTIVITY_NODE70 | -4.9993 | -2 | 148.5721 | 158.5028 | 0 | 0.00033111 | 3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR17 | Disconnect Switch | CONNECTIVITY_NODE20 | -2.3065 | -0.90444 | 12.5193 | 158.5816 | 0 | 2.3511e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR17 | Disconnect Switch | CONNECTIVITY_NODE31 | 2.3065 | 0.90444 | 12.5193 | -21.4184 | 0 | 2.3511e-06 | 0 | - | AA | Z1 | _CA_A1
T6 | 2W transformer | CONNECTIVITY_NODE57 | 2.5589 | 1.0732 | 14.027 | -22.7852 | 0 | 0.0012391 | 0.029713 | - | AA | Z1 | _CA_A1
T6 | 2W transformer | CONNECTIVITY_NODE60 | -2.5577 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.0012391 | 0.029713 | - | AA | Z1 | _CA_A1
L3_b | Line | CONNECTIVITY_NODE45 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 7.4972e-06 | 2.4366e-05 | - | AA | Z1 | _CA_A1
L3_b | Line | CONNECTIVITY_NODE48 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 7.4972e-06 | 2.4366e-05 | - | AA | Z1 | _CA_A1
DISCONNECTOR21 | Disconnect Switch | CONNECTIVITY_NODE24 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.2186e-08 | -6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR21 | Disconnect Switch | CONNECTIVITY_NODE37 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.2186e-08 | -6.5052e-17 | - | AA | Z1 | _CA_A1
BREAKER20 | Circuit breaker | CONNECTIVITY_NODE65 | 0.12304 | 0.18262 | 12.7132 | -56.0302 | 0 | 2.4244e-06 | 0 | - | AA | Z1 | _CA_A1
BREAKER20 | Circuit breaker | CONNECTIVITY_NODE66 | -0.12303 | -0.18262 | 12.7132 | 123.9698 | 0 | 2.4244e-06 | 0 | - | AA | Z1 | _CA_A1
Q1 | External grid | CONNECTIVITY_NODE82 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR27 | Disconnect Switch | CONNECTIVITY_NODE1 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.2673e-08 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR27 | Disconnect Switch | CONNECTIVITY_NODE46 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.2673e-08 | 0 | - | AA | Z1 | _CA_A1
L3_a | Line | CONNECTIVITY_NODE39 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 7.4972e-06 | 2.4366e-05 | - | AA | Z1 | _CA_A1
L3_a | Line | CONNECTIVITY_NODE42 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 7.4972e-06 | 2.4366e-05 | - | AA | Z1 | _CA_A1
DISCONNECTOR6 | Disconnect Switch | CONNECTIVITY_NODE11 | 9.1032 | 5.087 | 580.6551 | -29.7524 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR6 | Disconnect Switch | CONNECTIVITY_NODE12 | -9.0981 | -5.087 | 580.6551 | 150.2476 | 0 | 0.0050574 | -6.9389e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR49 | Disconnect Switch | CONNECTIVITY_NODE82 | 3.0328e-09 | 7.7882e-14 | 4.599e-09 | -90 | 0 | -8.1343e-09 | -6.6075e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR49 | Disconnect Switch | CONNECTIVITY_NODE83 | -1.1167e-08 | -7.7948e-14 | 1.6934e-08 | 90 | 0 | -8.1343e-09 | -6.6075e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR20 | Disconnect Switch | CONNECTIVITY_NODE35 | 2.3071 | 0.90628 | 12.5193 | -21.4184 | 0 | 2.3506e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR20 | Disconnect Switch | CONNECTIVITY_NODE36 | -2.3071 | -0.90628 | 12.5193 | 158.5816 | 0 | 2.3506e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR40 | Disconnect Switch | CONNECTIVITY_NODE66 | 0.12303 | 0.18262 | 12.7132 | -56.0302 | 0 | 2.4244e-06 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR40 | Disconnect Switch | CONNECTIVITY_NODE67 | -0.12303 | -0.18262 | 12.7132 | 123.9698 | 0 | 2.4244e-06 | 2.1684e-17 | - | AA | Z1 | _CA_A1
BREAKER6 | Circuit breaker | CONNECTIVITY_NODE21 | 1.6805 | 0.78474 | 9.3721 | -25.0384 | 0 | 1.317e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER6 | Circuit breaker | CONNECTIVITY_NODE22 | -1.6805 | -0.78474 | 9.3721 | 154.9616 | 0 | 1.317e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR39 | Disconnect Switch | CONNECTIVITY_NODE64 | 0.12304 | 0.18262 | 12.7132 | -56.0302 | 0 | 2.4244e-06 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR39 | Disconnect Switch | CONNECTIVITY_NODE65 | -0.12304 | -0.18262 | 12.7132 | 123.9698 | 0 | 2.4244e-06 | 2.1684e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR32 | Disconnect Switch | CONNECTIVITY_NODE53 | -2.5574 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR32 | Disconnect Switch | CONNECTIVITY_NODE54 | 2.5577 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | -3.4694e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR30 | Disconnect Switch | CONNECTIVITY_NODE50 | 2.5589 | 1.0732 | 14.027 | -22.7852 | 0 | 2.951e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR30 | Disconnect Switch | CONNECTIVITY_NODE51 | -2.5589 | -1.0732 | 14.027 | 157.2148 | 0 | 2.951e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR46 | Disconnect Switch | CONNECTIVITY_NODE77 | -2.5631e-11 | -2.6557e-18 | 5.1824e-10 | 90 | 0 | 1.3161e-11 | 6.7102e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR46 | Disconnect Switch | CONNECTIVITY_NODE78 | 3.8793e-11 | 3.3267e-18 | 7.8436e-10 | -90 | 0 | 1.3161e-11 | 6.7102e-19 | - | AA | Z1 | _CA_A1
DISCONNECTOR4 | Disconnect Switch | CONNECTIVITY_NODE7 | 2.6899 | 1.0646 | 14.6113 | -21.5647 | 0 | 3.2021e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR4 | Disconnect Switch | CONNECTIVITY_NODE8 | -2.6899 | -1.0646 | 14.6113 | 158.4353 | 0 | 3.2021e-06 | -1.7347e-16 | - | AA | Z1 | _CA_A1
BREAKER24 | Circuit breaker | CONNECTIVITY_NODE79 | -2.9588e-08 | 3.3139e-13 | 1.4956e-07 | 90 | 0 | -3.7756e-10 | -3.1132e-17 | - | AA | Z1 | _CA_A1
BREAKER24 | Circuit breaker | CONNECTIVITY_NODE80 | 2.921e-08 | -3.3142e-13 | 1.4765e-07 | -90 | 0 | -3.7756e-10 | -3.1132e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR41 | Disconnect Switch | CONNECTIVITY_NODE68 | 5 | 2 | 148.5721 | -21.4972 | 0 | 0.00033111 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR41 | Disconnect Switch | CONNECTIVITY_NODE69 | -4.9997 | -2 | 148.5721 | 158.5028 | 0 | 0.00033111 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR26 | Disconnect Switch | CONNECTIVITY_NODE44 | 0.37448 | 0.15093 | 2.0409 | -21.9815 | 0 | 6.3108e-08 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR26 | Disconnect Switch | CONNECTIVITY_NODE45 | -0.37448 | -0.15093 | 2.0409 | 158.0185 | 0 | 6.3108e-08 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR53 | Disconnect Switch | CONNECTIVITY_NODE24 | -2.963e-08 | 7.6106e-13 | 1.4977e-07 | 90 | 0 | -8.8648e-11 | 7.7e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR53 | Disconnect Switch | CONNECTIVITY_NODE89 | 2.9541e-08 | -7.6098e-13 | 1.4932e-07 | -90 | 0 | -8.8648e-11 | 7.7e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR35 | Disconnect Switch | CONNECTIVITY_NODE9 | -2.5566 | -1.0435 | 153.6293 | 157.2148 | 0 | 0.00035403 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR35 | Disconnect Switch | CONNECTIVITY_NODE58 | 2.557 | 1.0435 | 153.6293 | -22.7852 | 0 | 0.00035403 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR28 | Disconnect Switch | CONNECTIVITY_NODE47 | -0.37447 | -0.15091 | 2.0409 | 158.0185 | 0 | 6.2403e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR28 | Disconnect Switch | CONNECTIVITY_NODE48 | 0.37447 | 0.15091 | 2.0409 | -21.9815 | 0 | 6.2403e-08 | 6.5052e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR58 | Disconnect Switch | CONNECTIVITY_NODE97 | -9.8692e-10 | 1.6353e-17 | 1.4966e-09 | 90 | 0 | -9.8692e-10 | 1.6353e-17 | - | AA | Z1 | _CA_A1
DISCONNECTOR58 | Disconnect Switch | CONNECTIVITY_NODE98 | 0 | 0 | 0 | 90 | 0 | -9.8692e-10 | 1.6353e-17 | - | AA | Z1 | _CA_A1
L4 | Line | CONNECTIVITY_NODE19 | -1.6802 | -0.78372 | 9.3721 | 154.9616 | 0 | 0.00025297 | 0.0010224 | - | AA | Z1 | _CA_A1
L4 | Line | CONNECTIVITY_NODE23 | 1.6805 | 0.78474 | 9.3721 | -25.0384 | 0 | 0.00025297 | 0.0010224 | - | AA | Z1 | _CA_A1
DISCONNECTOR8 | Disconnect Switch | CONNECTIVITY_NODE15 | -9.0101 | -5 | 580.6551 | 150.2476 | 0 | 0.0050574 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR8 | Disconnect Switch | CONNECTIVITY_NODE16 | 9.0152 | 5 | 580.6551 | -29.7524 | 0 | 0.0050574 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR19 | Disconnect Switch | CONNECTIVITY_NODE5 | 2.3071 | 0.90628 | 12.5193 | -21.4184 | 0 | 2.3508e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR19 | Disconnect Switch | CONNECTIVITY_NODE34 | -2.3071 | -0.90628 | 12.5193 | 158.5816 | 0 | 2.3508e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR12 | Disconnect Switch | CONNECTIVITY_NODE22 | 1.6805 | 0.78474 | 9.3721 | -25.0384 | 0 | 1.3176e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
DISCONNECTOR12 | Disconnect Switch | CONNECTIVITY_NODE23 | -1.6805 | -0.78474 | 9.3721 | 154.9616 | 0 | 1.3176e-06 | 1.7347e-16 | - | AA | Z1 | _CA_A1
G3 | Synchronous machine | CONNECTIVITY_NODE9 | -4 | -3 | 278.1734 | 142.5477 | 50.5901 | 0 | 0 | - | AA | Z1 | _CA_A1
BREAKER28 | Circuit breaker | CONNECTIVITY_NODE93 | 2.995e-12 | 6.7205e-19 | 6.0555e-11 | -90 | 0 | -9.4924e-12 | 1.2356e-18 | - | AA | Z1 | _CA_A1
BREAKER28 | Circuit breaker | CONNECTIVITY_NODE94 | -1.2487e-11 | 5.6355e-19 | 2.5248e-10 | 90 | 0 | -9.4924e-12 | 1.2356e-18 | - | AA | Z1 | _CA_A1
M3 | Asynchronous machine | CONNECTIVITY_NODE13 | 5 | 3 | 328.8552 | -31.6616 | 97.6183 | 0 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR34 | Disconnect Switch | CONNECTIVITY_NODE56 | 2.5589 | 1.0732 | 14.027 | -22.7852 | 0 | 2.9507e-06 | 0 | - | AA | Z1 | _CA_A1
DISCONNECTOR34 | Disconnect Switch | CONNECTIVITY_NODE57 | -2.5589 | -1.0732 | 14.027 | 157.2148 | 0 | 2.9507e-06 | 0 | - | AA | Z1 | _CA_A1
M2b | Asynchronous machine | CONNECTIVITY_NODE13 | 2 | 1 | 126.1102 | -27.2628 | 93.9986 | 0 | 0 | - | AA | Z1 | _CA_A1
Q2 | External grid | CONNECTIVITY_NODE1 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | AA | Z1 | _CA_A1

## Phase to ground - IEC 60909-4
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node2
NodeCode: | 2
Code: | AAN2 110kV2
CIM ID: | _b3d3b4ad-02af-4490-8748-70f6c9a23734
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 15.9722 | /
Phase B: | / | / | 0 | /
Phase C: | / | / | 0 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 39.9641
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 15.972 | /
Phase B: | 0 | /
Phase C: | 0 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node3
NodeCode: | 3
Code: | AAN3 110kV3
CIM ID: | _c8726716-e182-4373-b83e-8f60070078cb
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 10.4106 | /
Phase B: | / | / | 0 | /
Phase C: | / | / | 0 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 24.2635
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 10.4106 | /
Phase B: | 0 | /
Phase C: | 0 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node4
NodeCode: | 4
Code: | AAN4 110kV4
CIM ID: | _c0adab49-d445-4609-a1a3-ebe4ef297cc8
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 9.0498 | /
Phase B: | / | / | 0 | /
Phase C: | / | / | 0 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 21.0415
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 9.0498 | /
Phase B: | 0 | /
Phase C: | 0 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node5
NodeCode: | 5
Code: | AAN5 110kV5
CIM ID: | _37edd845-456f-4c3e-98d5-19af0c1cef1e
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 17.0452 | /
Phase B: | / | / | 0 | /
Phase C: | / | / | 0 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 41.4303
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 17.0452 | /
Phase B: | 0 | /
Phase C: | 0 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /

## Three phase - IEC 60909-4
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node1
NodeCode: | 1
Code: | AAN1 380kV1
CIM ID: | _adee76cd-b2b9-48ac-8fd4-0d205a435f59
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 40.6447 | /
Phase B: | / | / | 40.6447 | /
Phase C: | / | / | 40.6447 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 100.5677
Phase B: | 100.5677
Phase C: | 100.5677
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 40.645 | /
Phase B: | 40.645 | /
Phase C: | 40.645 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node2
NodeCode: | 2
Code: | AAN2 110kV2
CIM ID: | _b3d3b4ad-02af-4490-8748-70f6c9a23734
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 31.7831 | /
Phase B: | / | / | 31.7831 | /
Phase C: | / | / | 31.7831 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 80.6079
Phase B: | 80.6079
Phase C: | 80.6079
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 31.57 | /
Phase B: | 31.57 | /
Phase C: | 31.57 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node3
NodeCode: | 3
Code: | AAN3 110kV3
CIM ID: | _c8726716-e182-4373-b83e-8f60070078cb
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 19.673 | /
Phase B: | / | / | 19.673 | /
Phase C: | / | / | 19.673 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 45.8111
Phase B: | 45.8111
Phase C: | 45.8111
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 19.388 | /
Phase B: | 19.388 | /
Phase C: | 19.388 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node4
NodeCode: | 4
Code: | AAN4 110kV4
CIM ID: | _c0adab49-d445-4609-a1a3-ebe4ef297cc8
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 16.2277 | /
Phase B: | / | / | 16.2277 | /
Phase C: | / | / | 16.2277 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 36.8427
Phase B: | 36.8427
Phase C: | 36.8427
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 16.017 | /
Phase B: | 16.017 | /
Phase C: | 16.017 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node5
NodeCode: | 5
Code: | AAN5 110kV5
CIM ID: | _37edd845-456f-4c3e-98d5-19af0c1cef1e
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 33.1894 | /
Phase B: | / | / | 33.1894 | /
Phase C: | / | / | 33.1894 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 83.4033
Phase B: | 83.4033
Phase C: | 83.4033
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 32.795 | /
Phase B: | 32.795 | /
Phase C: | 32.795 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node6
NodeCode: | 6
Code: | AAN6 10kV6
CIM ID: | _764e0b8a-f2af-4092-b6aa-b4a19e55db98
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 37.5629 | /
Phase B: | / | / | 37.5629 | /
Phase C: | / | / | 37.5629 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 98.1434
Phase B: | 98.1434
Phase C: | 98.1434
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 34.028 | /
Phase B: | 34.028 | /
Phase C: | 34.028 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node7
NodeCode: | 7
Code: | AAN7 10kV7
CIM ID: | _cd84fa40-ef63-422d-8ee0-d0a0f806719e
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 25.5895 | /
Phase B: | / | / | 25.5895 | /
Phase C: | / | / | 25.5895 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 51.6899
Phase B: | 51.6899
Phase C: | 51.6899
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 23.212 | /
Phase B: | 23.212 | /
Phase C: | 23.212 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Node8
NodeCode: | 8
Code: | AAN8 30kV8
CIM ID: | _87c0d153-e308-4b2b-92a4-4fad53ab1ff9
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | / | / | 13.5778 | /
Phase B: | / | / | 13.5778 | /
Phase C: | / | / | 13.5778 | /
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | / | / | / | /
Phase B: | / | / | / | /
Phase C: | / | / | / | /
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | / | / | / | / | /
Zn: | / | / | / | / | /
Zo: | / | / | / | / | /
#Peal Short Circuit
Ip[kA]
Phase A: | 36.9227
Phase B: | 36.9227
Phase C: | 36.9227
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 13.578 | /
Phase B: | 13.578 | /
Phase C: | 13.578 | /
#Impedance ratio
Ro\R: | /
Xo\X: | /
X\R | /
#Short Circuit Apparent Power
Sk"[MVA] | /

## Phase to Ground
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub1
NodeCode: | 1
Code: | AAS1 380kV1
CIM ID: | _adee76cd-b2b9-48ac-8fd4-0d205a435f59
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.987 | -23.9696 | 24.155 | -82.8967
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | -218.593 | -205.268 | 299.864 | -136.801
Phase C: | -218.594 | 212.737 | 305.025 | 135.778
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.58075 | 5.9102 | 5.9387 | 84.388 | 10.1769
Zn: | 0.58073 | 5.9106 | 5.939 | 84.3886 | 10.1779
Zo: | 2.5449 | 17.9221 | 18.1019 | 81.918 | 7.0422
#Peal Short Circuit
Iac[kA]
Phase A: | 57.8786
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 24.155 | 1.1541e-17
Phase B: | 0 | 0
Phase C: | 0 | 0
#Impedance ratio
Ro\R: | 4.3822
Xo\X: | 3.0324
X\R | 10.1769
#Short Circuit Apparent Power
Sk"[MVA] | 5299.45
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub1
NodeCode: | 2
Code: | AAS1 110kV2
CIM ID: | _b3d3b4ad-02af-4490-8748-70f6c9a23734
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 1.6333 | -15.8943 | 15.978 | -84.1329
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | -1.89296e-007 | 1.89972e-007 | 2.68184e-007 | 134.898
Phase B: | -69.5601 | -59.6832 | 91.6553 | -139.37
Phase C: | -69.5664 | 61.3363 | 92.745 | 138.598
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.17414 | 2.1973 | 2.2042 | 85.4688 | 12.6183
Zn: | 0.17367 | 2.1995 | 2.2063 | 85.4852 | 12.6645
Zo: | 0.993 | 8.6512 | 8.708 | 83.4522 | 8.7122
#Peal Short Circuit
Iac[kA]
Phase A: | 39.3178
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 15.978 | 1.32531e-014
Phase B: | 0 | 0
Phase C: | 0 | 0
#Impedance ratio
Ro\R: | 5.7024
Xo\X: | 3.9372
X\R | 12.6183
#Short Circuit Apparent Power
Sk"[MVA] | 1014.74
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub2
NodeCode: | 3
Code: | AAS2 110kV3
CIM ID: | _c8726716-e182-4373-b83e-8f60070078cb
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 1.5878 | -10.2732 | 10.3951 | -81.2139
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | -5.5453e-007 | 3.73739e-007 | 6.68718e-007 | 146.021
Phase B: | -67.6778 | -60.2359 | 90.6016 | -138.33
Phase C: | -67.7004 | 60.6555 | 90.8979 | 138.142
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.52845 | 3.5388 | 3.5781 | 81.5068 | 6.6966
Zn: | 0.52196 | 3.5215 | 3.56 | 81.569 | 6.7467
Zo: | 2.0291 | 12.8642 | 13.0233 | 81.0363 | 6.3398
#Peal Short Circuit
Iac[kA]
Phase A: | 24.0564
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 10.3951 | 1.80872e-022
Phase B: | 0 | 0
Phase C: | 0 | 0
#Impedance ratio
Ro\R: | 3.8398
Xo\X: | 3.6352
X\R | 6.6966
#Short Circuit Apparent Power
Sk"[MVA] | 660.18
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub3
NodeCode: | 4
Code: | AAS3 110kV4
CIM ID: | _c0adab49-d445-4609-a1a3-ebe4ef297cc8
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 1.4043 | -8.9315 | 9.0412 | -81.0644
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 3.58398e-008 | 2.96279e-008 | 4.65006e-008 | 39.5797
Phase B: | -65.7575 | -61.0556 | 89.732 | -137.123
Phase C: | -65.7664 | 59.9064 | 88.9607 | 137.67
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.73466 | 4.2578 | 4.3207 | 80.2103 | 5.7956
Zn: | 0.73184 | 4.2509 | 4.3134 | 80.2315 | 5.8084
Zo: | 2.134 | 14.3903 | 14.5477 | 81.565 | 6.7434
#Peal Short Circuit
Iac[kA]
Phase A: | 20.8602
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 9.0412 | 6.31874e-023
Phase B: | 0 | 0
Phase C: | 0 | 0
#Impedance ratio
Ro\R: | 2.9047
Xo\X: | 3.3798
X\R | 5.7956
#Short Circuit Apparent Power
Sk"[MVA] | 574.195
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub4
NodeCode: | 5
Code: | AAS4 110kV5
CIM ID: | _37edd845-456f-4c3e-98d5-19af0c1cef1e
#Fault Data
Type: | L_G
Fault Phase(s): | PH_A
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.0214 | -16.9089 | 17.0293 | -83.183
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 8.48505e-007 | -7.9947e-007 | 1.16581e-006 | -43.2957
Phase B: | -68.7996 | -59.2423 | 90.7912 | -139.269
Phase C: | -68.8046 | 61.8072 | 92.4889 | 138.067
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.17602 | 2.1047 | 2.1121 | 85.2195 | 11.9576
Zn: | 0.17611 | 2.1098 | 2.1171 | 85.2283 | 11.9798
Zo: | 1.1087 | 8.0054 | 8.0818 | 82.1151 | 7.2206
#Peal Short Circuit
Iac[kA]
Phase A: | 41.0534
Phase B: | 0
Phase C: | 0
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 17.0293 | 4.59322e-017
Phase B: | 0 | 0
Phase C: | 0 | 0
#Impedance ratio
Ro\R: | 6.2988
Xo\X: | 3.8036
X\R | 11.9576
#Short Circuit Apparent Power
Sk"[MVA] | 1081.51

## Three phase
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub1
NodeCode: | 1
Code: | AAS1 380kV1
CIM ID: | _adee76cd-b2b9-48ac-8fd4-0d205a435f59
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 3.974 | -40.4427 | 40.6375 | -84.388
Phase B: | -37.0114 | 16.7798 | 40.6375 | 155.612
Phase C: | 33.0374 | 23.6629 | 40.6375 | 35.612
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.58075 | 5.9102 | 5.9387 | 84.388 | 10.1769
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 100.561
Phase B: | 100.561
Phase C: | 100.561
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 40.6324 | 1.5647e-13
Phase B: | 40.6324 | 1.5647e-13
Phase C: | 40.6324 | 1.5647e-13
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 10.1769
#Short Circuit Apparent Power
Sk"[MVA] | 26746.7
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub1
NodeCode: | 2
Code: | AAS1 110kV2
CIM ID: | _b3d3b4ad-02af-4490-8748-70f6c9a23734
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.5039 | -31.5948 | 31.6939 | -85.4688
Phase B: | -28.6139 | 13.629 | 31.6939 | 154.531
Phase C: | 26.11 | 17.9658 | 31.6939 | 34.5312
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.17414 | 2.1973 | 2.2042 | 85.4688 | 12.6183
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 80.3492
Phase B: | 80.3492
Phase C: | 80.3492
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 31.4926 | 8.0267e-11
Phase B: | 31.4926 | 8.0267e-11
Phase C: | 31.4926 | 8.0267e-11
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 12.6183
#Short Circuit Apparent Power
Sk"[MVA] | 6038.49
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub2
NodeCode: | 3
Code: | AAS2 110kV3
CIM ID: | _c8726716-e182-4373-b83e-8f60070078cb
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.8836 | -19.3102 | 19.5243 | -81.5068
Phase B: | -18.1649 | 7.1578 | 19.5243 | 158.493
Phase C: | 15.2814 | 12.1524 | 19.5243 | 38.4932
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.52845 | 3.5388 | 3.5781 | 81.5068 | 6.6966
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 45.4524
Phase B: | 45.4524
Phase C: | 45.4524
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 19.266 | 2.0252e-21
Phase B: | 19.266 | 2.0252e-21
Phase C: | 19.266 | 2.0252e-21
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 6.6966
#Short Circuit Apparent Power
Sk"[MVA] | 3719.89
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub3
NodeCode: | 4
Code: | AAS3 110kV4
CIM ID: | _c0adab49-d445-4609-a1a3-ebe4ef297cc8
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.7492 | -15.9331 | 16.1686 | -80.2103
Phase B: | -15.1731 | 5.5857 | 16.1686 | 159.79
Phase C: | 12.4239 | 10.3474 | 16.1686 | 39.7897
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.73466 | 4.2578 | 4.3207 | 80.2103 | 5.7956
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 36.677
Phase B: | 36.677
Phase C: | 36.677
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 15.9559 | 6.0739e-25
Phase B: | 15.9559 | 6.0739e-25
Phase C: | 15.9559 | 6.0739e-25
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 5.7956
#Short Circuit Apparent Power
Sk"[MVA] | 3080.52
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub4
NodeCode: | 5
Code: | AAS4 110kV5
CIM ID: | _37edd845-456f-4c3e-98d5-19af0c1cef1e
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 2.7565 | -32.9614 | 33.0764 | -85.2195
Phase B: | -29.9236 | 14.0935 | 33.0764 | 154.78
Phase C: | 27.1671 | 18.8679 | 33.0764 | 34.7805
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.17602 | 2.1047 | 2.1121 | 85.2195 | 11.9576
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 83.3825
Phase B: | 83.3825
Phase C: | 83.3825
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 32.7002 | 1.8793e-11
Phase B: | 32.7002 | 1.8793e-11
Phase C: | 32.7002 | 1.8793e-11
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 11.9576
#Short Circuit Apparent Power
Sk"[MVA] | 6301.91
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub4
NodeCode: | 6
Code: | AAS4 10kV6
CIM ID: | _764e0b8a-f2af-4092-b6aa-b4a19e55db98
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 1.8197 | -37.5106 | 37.5547 | -87.2227
Phase B: | -33.395 | 17.1794 | 37.5547 | 152.777
Phase C: | 31.5753 | 20.3312 | 37.5547 | 32.7773
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.008194 | 0.16891 | 0.16911 | 87.2227 | 20.6139
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 99.1715
Phase B: | 99.1715
Phase C: | 99.1715
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 34.0219 | 3.4243e-06
Phase B: | 34.0219 | 3.4243e-06
Phase C: | 34.0219 | 3.4243e-06
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 20.6139
#Short Circuit Apparent Power
Sk"[MVA] | 650.467
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub5
NodeCode: | 7
Code: | AAS5 10kV7
CIM ID: | _cd84fa40-ef63-422d-8ee0-d0a0f806719e
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 7.3226 | -24.516 | 25.5862 | -73.3698
Phase B: | -24.8927 | 5.9164 | 25.5862 | 166.63
Phase C: | 17.5701 | 18.5995 | 25.5862 | 46.6302
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.071037 | 0.23783 | 0.24821 | 73.3698 | 3.348
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 51.3821
Phase B: | 51.3821
Phase C: | 51.3821
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 23.2139 | 1.9338e-43
Phase B: | 23.2139 | 1.9338e-43
Phase C: | 23.2139 | 1.9338e-43
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 3.348
#Short Circuit Apparent Power
Sk"[MVA] | 443.166
##Fault Calculation function Results at fault location
Element Type: | Node
Area: | AA
Substation: | Sub1
NodeCode: | 8
Code: | AAS1 30kV8
CIM ID: | _87c0d153-e308-4b2b-92a4-4fad53ab1ff9
#Fault Data
Type: | L_L_L
Fault Phase(s): | PH_A_B_C
Arc Impedance: | 0
#Current at fault location
| Re(Ik")[kA] | Im(Ik")[kA] | Ik"[kA] | Angle[o]
Phase A: | 0.36814 | -13.627 | 13.632 | -88.4525
Phase B: | -11.9854 | 6.4947 | 13.632 | 151.548
Phase C: | 11.6173 | 7.1323 | 13.632 | 31.5475
#Voltage at fault location
| Re(Vk")[kV] | Im(Vk")[kV] | Vk"[kV] | Angle[o]
Phase A: | 0 | 0 | 0 | 0
Phase B: | 0 | 0 | 0 | 0
Phase C: | 0 | 0 | 0 | 0
#Impedance
| Real[ohm] | Imaginary[ohm] | Module[ohm] | Angle[o] | X/R
Zp: | 0.037745 | 1.3971 | 1.3976 | 88.4525 | 37.0154
Zn: | 0 | 0 | 0 | 0 | 0
Zo: | 0 | 0 | 0 | 0 | 0
#Peal Short Circuit
Iac[kA]
Phase A: | 37.0863
Phase B: | 37.0863
Phase C: | 37.0863
#Braking Short Circuit
| Ib[kA] | Idc[kA]
Phase A: | 13.6306 | 0.0019082
Phase B: | 13.6306 | 0.0019082
Phase C: | 13.6306 | 0.0019082
#Impedance ratio
Ro\R: | 0
Xo\X: | 0
X\R | 37.0154
#Short Circuit Apparent Power
Sk"[MVA] | 708.339

## ShortCircuit results diagrams
High-voltage a.c. test network 380 kV/110 kV/30 kV/10 kV (IEC 60909-4) with added three phase short circuit results
High-voltage a.c. test network 380 kV/110 kV/30 kV/10 kV (IEC 60909-4) with added one phase short circuit results
Three Phase Short Circuit
Phase to Ground Short Circuit