Explicit Power Flow calculation

Version: 3

CGMES 3.0

14 October 2021

Contents

1.	Introduction	2

2.	General flow equations in a branch	3

3.	Analytical solution for small grids	4

3.1.	One generation, one load, one branch	4

3.2.	One generation, one load, two similar branches	5

4.	Numerical solution for small grids	7

4.1.	One generation, one load, two similar branches	7

5.	Mapping to CIM classes and attributes	8

Introduction

This document describes the general equations for a load flow model with two nodes and a branch in section 2.

These equations are used to derive the resulting voltage and angle for two general cases in section 3.

An example is given in section 4 with the details of the exact numerical solution.

Section 5 provides the mapping between the attributes used in the equations and the CIM classes and attributes from the ENTSO-E Common Grid Model Exchange Standard (CGMES) version 3.0.

General flow equations in a branch

Let us define a generic branch with its direct components from point i to point j as in the following diagram:

ρiejαi

Vi

ρjejαj

X

R

Vk

Gi

Bi

Gj

Bj

Vm

Vj

Ik

Im

I

Ik.sh

Im.sh

The voltages are expressed with their magnitudes and angles as follows:

Vi=Viejθi  ;  Vj=Vjejθj

The phase and ratio shifts on sides i and j give the following equations:

Vk=Vi ρiejαi  ;  Vm=Vj ρjejαj

The apparent power taken in k and flowing to m is calculated as follows:

Skm=3Vk Ik*  where  Ik=I+Ik.sh

And  I=Vk-VmR+jX  and  Ik.sh= Vk Gi+jBi

Let us define the following constants:

δ=arctanRX  and  Y=1R+jX=Yejδ-π2

Therefore:

Skm= 3VkVk-Vm Y + Vk Gi+jBi *

Skm= 3VkVk*-Vm*Y *+ Vk* Gi-jBi

Skm= -3Vk Vm* Y* + 3Vk Vk*Y*+Gi-jBi

Skm= -3ρi(1ρj)ViVjYejπ2-δ+θi-θj+αi+αj+ 3ρi2Vi2Yejπ2-δ+Gi-jBi

Knowing:

Ui=3Vi  and Uj=3Vj

Pij=Pkm=ReSkm  and Qij=Qkm=ImSkm

We obtain:

Pij=ρi(1/ρj)UiUjYsinθi-θj+αi+αj-δ+ ρi2Ui2Ysinδ+GiQij=-ρi(1ρj)UiUjYcos(θi-θj+αi+αj-δ)+ ρi2Ui2Ycosδ-Bi

Analytical solution for small grids

One generation, one load, one branch

Inputs for the calculation are:

- On the left side (load):

  - Active injection Pi

  - Reactive injection Qi

- On the right side (generation):

  - Voltage setpoint Uj

  - Angle reference θj

The outputs will be:

- On the left side (load):

  - Voltage at load Ui

  - Angle at load θi

ρiejαi

ρjejαj

Pi,Qi

Ui,θi

X

R

Gi

Bi

Gj

Bj

Uj,θj

The general equation taken at i gives the following:

Pi=ρiρjUiUjYsinθi-θj+αi-αj-δ+ ρi2Ui2Ysinδ+GiQi=-ρiρjUiUjYcos(θi-θj+αi-αj-δ)+ ρi2Ui2Ycosδ-Bi

We would like to evaluate Ui so we square both equations and do the sum:

Pi-ρi2Ui2Ysinδ+Gi2 =ρiρjUiUjY2 sin2θi-θj+αi-αj-δQi-ρi2Ui2Ycosδ-Bi2=ρiρjUiUjY2cos2(θi-θj+αi-αj-δ)

Pi-ρi2Ui2Ysinδ+Gi2+Qi-ρi2Ui2Ycosδ-Bi2=ρiρjUiUjY2

We obtain a biquadratic function of Ui which can be expressed as follows: AUi4+BUi2+C=0

Where: A=ρi4Ysinδ+Gi2+Ycosδ-Bi2B=-ρi22PiYsinδ+Gi+2QiYcosδ-Bi+ρjUjY2C=Pi2+Qi2

And the solution: Ui= -B+B2-4AC2A

Given Ui, we then have: θi=θj-αi+αj+δ+arcsinPi-ρi2Ui2Ysinδ+GiρiρjUiUjY

One generation, one load, two similar branches

Inputs and outputs are the same as in previous case.

We consider two parallel branches with the same electrical parameters (R,X, Bi, Gi, Bj, Gj) but with different tap settings (ρi1, αi1, ρi2, αi2, ρj1, αj1, ρj2, αj2).

ρi2ejαi2

ρj2ejαj2

X

R

Gi

Bi

Gj

Bj

ρi1ejαi1

ρj1ejαj1

Pi,Qi

Ui,θi

X

R

Gi

Bi

Gj

Bj

Uj,θj

As the flows from each branch add up, the general equation taken at i gives the following:

Pi=ρi1ρj1UiUjYsinθi-θj+αi1-αj1-δ+ ρi12Ui2Ysinδ+Gi    + ρi2ρj2UiUjYsinθi-θj+αi2-αj2-δ+ ρi22Ui2Ysinδ+GiQi=-ρi1ρj1UiUjYcosθi-θj+αi1-αj1-δ+ ρi12Ui2Ycosδ-Bi          -ρi2ρj2UiUjYcos(θi-θj+αi2-αj2-δ)+ ρi22Ui2Ycosδ-Bi

We would like to evaluate Ui so we square both equations and do the sum:

Pi-Ui2(ρi12+ρi22)Ysinδ+Gi2 =UiUjY2 ρi12ρj12sin2θi-θj+αi1-αj1-δ+ρi22ρj22sin2θi-θj+αi2-αj2-δ+ 2ρi1ρj1ρi2ρj2sinθi-θj+αi1-αj1-δsinθi-θj+αi2-αj2-δQi-Ui2(ρi12+ρi22)Ycosδ-Bi2=UiUjY2ρi12ρj12cos2θi-θj+αi1-αj1-δ+ρi22ρj22cos2θi-θj+αi2-αj2-δ+2ρi1ρj1ρi2ρj2cosθi-θj+αi1-αj1-δcosθi-θj+αi2-αj2-δ

Pi-Ui2Ysinδ+Gi(ρi12+ρi22)2+Qi-Ui2Ycosδ-Bi(ρi12+ρi22)2=UiUjY2ρi12ρj12+ρi22ρj22+2ρi1ρj1ρi2ρj2cosαi1-αj1-αi2+αj2

We obtain a biquadratic function of Ui which can be expressed as follows: AUi4+BUi2+C=0

Where: A=(ρi12+ρi22)2Ysinδ+Gi2+Ycosδ-Bi2B=-2ρi12+ρi22PiYsinδ+Gi+QiYcosδ-Bi-UjY2ρi12ρj12+ρi22ρj22+2ρi1ρj1ρi2ρj2cosαi1-αj1-αi2+αj2C=Pi2+Qi2

And the solution: Ui= -B+B2-4AC2A

Given Ui, we then want to calculate θi out of Pi expression:

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYρi1ρj1sinθi-θj+αi1-αj1-δ+ ρi2ρj2sinθi-θj+αi2-αj2-δ

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYρi1ρj1sinθi-θj-δcosαi1-αj1+ρi1ρj1cosθi-θj-δsinαi1-αj1+ρi2ρj2sinθi-θj-δcosαi2-αj2+ρi2ρj2cosθi-θj-δsinαi2-αj2

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYρi1ρj1cosαi1-αj1+ρi2ρj2cosαi2-αj2sinθi-θj-δ+ρi1ρj1sinαi1-αj1+ρi2ρj2sinαi2-αj2cosθi-θj-δ

Let us define the following constants:

D= ρi1ρj1sinαi1-αj1+ρi2ρj2sinαi2-αj2E=ρi1ρj1cosαi1-αj1+ρi2ρj2cosαi2-αj2

tanγ=DE

Therefore:

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYEsinθi-θj-δ+Dcosθi-θj-δ

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYEsinθi-θj-δ+tanγcosθi-θj-δ

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYEcosγcos⁡(γ)sinθi-θj-δ+sinγcosθi-θj-δ

Pi=ρi12+ρi22Ui2Ysinδ+Gi+UiUjYEcos⁡(γ)sinγ+θi-θj-δ

Since: Ecosγ=EcosarctanDE=E1+DE2=E2+D2

Finally we obtain:

θi=θj+δ-arctanDE+ arcsin⁡Pi-ρi12+ρi22Ui2Ysinδ+GiUiUjYE2+D2

Numerical solution for small grids

One generation, one load, two similar branches

We consider the following small grid.

ρj2ejαj2

X

R

Pi,Qi

Ui,θi

X

R

Uj,θj

The result can be derived directly from section 4.2 with the following parameter values:

- Pi=-332 MWQi=-78 MVAR                    R= 4,1956 Ω X=12,73  Ωρj2=0,997829αj2=-3,77605°                    Uj= 397,1 kV θj=0°

The load P and Q in the equations follow generator convention, i.e. opposite to the CGMES.

All other parameters do not appear: Bi=Gi=Bj=Gj=αi1=αi2=αj1=0 and ρi1=ρi2=ρj1=1

We can calculate: δ=arctanRX=0,3184  and  Y=1R2+X2=0,0746 Ω-1

We solve the biquadratic function of Ui:

Pi-2Ui2Ysinδ2+Qi-2Ui2Ycosδ2=UiUjY21+1/ρj22+2(1ρj2)cos⁡(-αj2)

Where: A=4Y2=0,0223B=-4YPisinδ+Qicosδ-UjY21+1/ρj22+2(1/ρj2)cos⁡(-αj2)= -3461,6C=Pi2+Qi2=116308

The solution is: Ui= -B+B2-4AC2A

- Ui=394,26 kV

We can calculate: D= (1/ρj2)sinαj2=0,066E=1+(1/ρj2)cosαj2=2

The solution is: θi=δ-arctanDE+arcsinPi-2Ui2YsinδUiUjYE2+D2

- θi=1,18°

Mapping to CIM classes and attributes

| Attribute | CIM attribute |
| --- | --- |
| R | cim:ACLineSegment.r or cim:PowerTransformerEnd.r |
| X | cim:ACLineSegment.x or cim:PowerTransformerEnd.x |
| B | cim:ACLineSegment.bch or cim:PowerTransformerEnd.b (CIM only supports cases in which Bi=Bj) |
| G | cim:ACLineSegment.gch or cim:PowerTransformerEnd.g (CIM only supports cases in which Gi=Gj) |
| ρ | cim:TapChangerTablePoint.ratio |
| α | cim:PhaseTapChangerTablePoint.angle |
| U | cim:SvVoltage.v |
| θ | cim:SvVoltage.angle |
| P | cim:EnergyConsumer.p or cim:RotatingMachine.p |
| Q | cim:EnergyConsumer.q or cim:RotatingMachine.q |