## Svedala
Rule | Group | Type | Model | Class | Recurrence | Description | Comment
C:600:ALL:NA:PROF10 | 600-1 | Warning | Svedala_EQ | md:FullModel | 1/1 | For complete validation, the boundary set (BS) should be included. Otherwise references to BS could be reported as errors and some of the validation may not be performed.
|  | Warning | Svedala_EQ |  | N/A | No boundary connections are found. The IGM is an island without any inter-connections.
|  | Warning | Svedala_EQ | ControlArea | 1/1 | The ControlArea doesn't contain any child instances (or is not referenced by other instances).
|  | Warning | Svedala_EQ | ACLineSegment | 29/90 | At least one of the associated OperationalLimits is violated.
|  | Warning | Svedala_EQ | PowerTransformer | 18/53 | At least one of the associated OperationalLimits is violated.
|  | Warning | Svedala_SSH | RegulatingControl | 4/87 | The target voltage specified in the RegulatingControl doesn't match the nominal voltage of the regulated ConnectivityNode. The difference is between 10%-20%.
|  | Warning | Svedala_SSH | RegulatingControl | 4/87 | The target voltage specified in the RegulatingControl doesn't match the nominal voltage of the regulated TopologicalNode. The difference is between 10%-20%.
C:600:ALL:NA:PROF10 | 600-1 | Error | Svedala_SV | md:FullModel | 1/1 | Unable to find the Topology model part this model is dependent on. Because of the missing or invalid model dependency description, the performed validation may be incomplete. | Due to CIMdesk issue
|  | Warning | Svedala_SV | md:FullModel | 1/1 | unknown_type: Svedala_TP is unexpected to appear in the Model.DependentOn statements. | Due to CIMdesk issue
|  | Warning | Svedala_DL | md:FullModel | 1/1 | unknown_type: Svedala_TP is unexpected to appear in the Model.DependentOn statements. | Due to CIMdesk issue